## Slide 1: Best Ever Alarm System Toolkit
Kay Kasemir,
Xihui Chen,
Katia Danilova
SNS/ORNL
kasemirk@ornl.gov
April, 2013

## Slide 2: What is BEAST?
Control System
Alarm Server
Cool UI
Configuration
An alarm system that monitors Process Variables (PVs) in a Control System
Effectively help operators take the correct action at the correct time.

## Slide 3: Architecture
IOCs
Alarm Cfg & State
RDB
FECs/IOCs
Alarm Server
Current Alarms: Latched? Annunciated? Acknowledged?
LOG
Message RDB
JMS to Speech
JMS to RDB
Tomcat
Reports
Alarm Client GUI
JMS
Alarm Updates
Ack’; Config Updates
Annunciations
Log Messages
TALK
ALARM_CLIENT
ALARM_SERVER
PV Updates (Channel Access, …)

## Slide 4: Levels Of Complexity
Use the Alarm System
  Control Room operator
Configure the Alarm System
  Certain operators, IOC engineers
Alarm System Setup
  CSS maintainer for site
Coming up with a good configuration
  Everybody
Easy
Hard

## Slide 5: Client GUI: Alarm Area Panel
An overview of all alarm areas
Acknowledge the whole area

## Slide 6: Client GUI: Alarm Table
All current alarms
  active
  ack’ed
Optional: Voice Annunciation
Sort by column
Acknowledge one or multiple alarms
  Select by PV or description
  BNL/RHIC type un-ack’

## Slide 7: Client GUI: Alarm Tree
See complete configuration
  Active, ack’ed, inactive, disabled
Hierarchical
  Optionally only show active alarms
  Ack’/Un-ack’ PVs or sub-tree

## Slide 8: Guidance, Related Displays, Commands
View Guidance Texts
Start related displays (EDM)
Open Web pages
Run ext. commands
Hierarchical: Including info of parent entries
Merges Guidance etc. from all selected alarms

## Slide 9: CSS Integration: Alarm  Data Browser
Context menu: Alarm Duration, Guidance, Displays, …
Select Data Browser for PV in alarm
View history, annotate
3
2
1

## Slide 10: Data Browser  Electronic Logbook
After inspecting alarm PV’s history, post commented plot to E-Log

## Slide 11: Directly from Alarm to E-Log
“Logbook” from context menu creates text w/ basic info about selected alarms. Edit, submit.

## Slide 12: Online Configuration Changes
.. may require Authentication/Authorization (LDAP)
Log in/out

## Slide 13: Configure PV
formula-based alarm enablement
Latch highest severity, require acknowledgement
Chatter filter

## Slide 14: Logging
..into generic CSS log also used for error/warn/info/debug messages
Alarm Server: State transitions, Annunciations
Alarm GUI: Ack/Un-Ack requests, Config changes
Generic Message History Viewer
  Example w/ Filter on TEXT=CONFIG

## Slide 15: Logging: Get timeline
Filter on TYPE, PV
1. PV triggers, clears, triggers again
2. Alarm Server latches alarm
4. Problem fixed
3. Alarm Server annunciates
5. Ack’ed by operator
6. All OK

## Slide 16: Web Report Examples
Examples from SNS
  Code would need some rework to port to other sites

## Slide 17: Creating a good Alarm Configuration
B. Hollifield, E. Habibi, "Alarm Management: Seven Effective Methods for Optimum Performance", ISA, 2007
Hard

## Slide 18: Alarm Philosophy
Goal: Help operators take correct actions
  Alarms with guidance, related displays
  Manageable alarm rate (<150/day)
  Operators will respond to every alarm (corollary to manageable rate)

## Slide 19: What’s a valid alarm?
DOES IT REQUIRE IMMEDIATE OPERATOR ACTION?
  What action? Alarm guidance!
    Not “make elog entry”, “tell next shift”, …
  Consequence of not reacting?
  How much time to react?

## Slide 20: How are alarms added?
Alarm triggers: PVs on IOCs
  But more than just setting HIGH, HIHI, HSV, HHSV
  HYST (alarm deadband) is good idea
  Dynamic limits, enable based on machine state,...
  Requires thought, communication, documentation
Added to alarm server with
  Guidance: How to respond
  Related screen: Reason for alarm (limits, …), link to screens mentioned in guidance
  Link to rationalization info (wiki)

## Slide 21: Example: Elevated Temp/Press/Res.Err./…
Immediate action required?
  Do something to prevent interlock trip
Impact, Consequence?
  Beam off if interlock tripped
Time to respond?
  10 minutes to prevent interlock
  
MINOR? MAJOR?
Guidance: “Open Valve 47 a bit, …”
Related Displays: Screen that shows Temp, Valve, …

## Slide 22: Avoid Multiple Alarm Levels
Analog PVs for Temp/Press/Res.Err./…:
  Easy to set LOLO, LOW, HIGH, HIHI
Consider:
  Do they require significantly different operator actions?
  Will there be a lot of time after the HIGH to react before a follow-up HIHI alarm?
In most cases, HIGH & HIHI only double the alarm traffic
  Set only HSV to generate single, early alarm
  Adding HHSV alarm assuming that the first one is ignored only worsens the problem

## Slide 23: Alarms for Redundant Pumps

## Slide 24: Alarm Generation: Redundant Pumps the wrong way
Control System
  Pump1 on/off status
  Pump2 on/off status
Simple Config setting: Pump Off => Alarm:
  It’s normal for the ‘backup’ to be off
  Both running is usually bad as well
    Except during tests or switchover
  During maintenance, both can be off

## Slide 25: Redundant Pumps
Control System
  Pump1 on/off status
  Pump2 on/off status
  Number of running pumps
  Configurable number of desired pumps
Alarm System: Running == Desired?
  … with delay to handle tests, switchover
Same applies to devices that are only needed on-demand
1
Required Pumps:

## Slide 26: Weekly Review: How Many? Top 10?

## Slide 27: Summary
Easy to use
  Check alarms in Table, Tree, Panel
  Fix it: Read Guidance, use Display Links
  ✔Acknowledge
Configuration
  Can be changed on the fly
  Operators can update guidance or add better display links
Alarm System Setup
  Somewhat Involved, but only once
Coming up with a good configuration
  Hard
Easy
Hard

## Slide 28: Thank You!
BEAST Home Page:
  http://sourceforge.net/apps/trac/cs-studio/wiki/BEAST
See also:
  B. Hollifield, E. Habibi, "Alarm Management: Seven Effective Methods for Optimum Performance", ISA, 2007
  Alarm Rationalization: Practical Experience Rationalizing Alarm Configuration for an Accelerator SubSystem, Xiaosong Geng, etc,. http://info.ornl.gov/sites/publications/files/Pub22522.PDF